|  |  |  |  |
| --- | --- | --- | --- |
| **Capess** | |  | |
|  | | **capess3-1** |  |
| **FEATURES** | |  |  |
| \* EM series battery cells  \* Safest technology  \* Ultra long cycle life  \* Extreme temperature  \* Easy to install  \* Rarely maintenance | |  |  |
| **PART NUMBER** | **GTEM-48V7500-E** | | |
| Energy storage | 7.5kWh | | |
| Capacity | 147Ah | | |
| Nominal Voltage | 51.8V/DC | | |
| Maximum Charge Voltage | 58V/DC | | |
| Discharge Cut-off Voltage | 42V/DC | | |
| Internal Configuration | 14S7P/EM21 | | |
| ESR/AC @1KHz 50% SOC | <10mΩ | | |
| Max. Continuous Charge Current | 100A | | |
| Max. Continuous Discharge Current | 100A | | |
| Cells Self-discharge Rate | 2% per month | | |
| Round Trip Efficiency\*1 | 97.8% | | |
| Projected cycle life(25℃) | 20000 times | | |
| Projected life(25℃) | 15 years | | |
| Recommended Depth of Discharge | ≤90% | | |
| Maximum Depth of Discharge | 100% | | |
| Cooling Method | Natural | | |
| Shell Material | Metal & ABS plastic | | |
| Parallel Connection | Up to 16 sets | | |
| Compatible Protocol | CAN,RS485 | | |
| Monitoring Data | System voltage,current,temperature,SOC,SOH,cycle,cell’s voltage | | |


|  |  |
| --- | --- |
| **ENVIRONMENTAL SPECIFICATIONS** | |
| Ingress Rating | Indoor IP20 |
| Operating Humidity | 0~90% RH Non-condensing |
| Charge Temperature | 0℃~+55℃ |
| Discharge Temperature | -20℃~+60℃ |
| Storage Conditions | SOC>30%,-20℃~+40℃,25% ~ 95%RH,  One full charge needed per two months |
| Transport Conditions | 50% SOC,-20℃~+40℃ |
| Maximum Elevation | 3000m (9843ft) |

|  |  |
| --- | --- |
| **COMPLIANCE INFORMATION** | |
| IEC\*2 | IEC62619 |
| Italy | CEI0-21:2022 |
| CE | EN 62133:2013,  EN 55032:2015+AC:2016,  EN 55035:2017,  EN 61000-3-2:2014, |
| Transport | UN38.3,MSDS |
| Environmental | RoHS |

Remark:\*1 (1)At room temperature 25℃, charge-discharge at 100A.(2)Limited charge at 100A for resident energy storage, (3)At the beginning of life. \*2on testing,certificate will come soon.

|  |  |  |
| --- | --- | --- |
| **MECHANICAL SPECIFICATIONS** | | |
| Part Number | **GTEM-48V7500-E** | |
| Weight | 50Kg | |
| Dimensions(WxDxH) | 470x520x170(mm) | |
| Mount Options | On rack cabinet | |
| Dimensions and weight differ slightly for each batch. Contact Green Tech for additional information. | |
| 5 | |

|  |
| --- |
| **CHARGING-DISCHARGING CURVE** |

****

**Note：**If the charger needs to set the floating charge voltage, it is recommended to set the U Float value to 57V.



|  |
| --- |
| **Bluetooth Display Function** |

This Bluetooth APP can be operated by both Android and IOS. It establish a Bluetooth connection between your smart phone and the battery, usages includes below: managing the battery pack, gathering the data and

displaying them, conducting modifications on settings.

Bluetooth APP can achieve below functions:

* Display the basic data of battery pack
* Modifying the communication between BMS and inverter
* Setting Alert Parameters and Switch on/off
* Support Single and Parallel operation
* Shift between Chinese and English

****