## rev. 05.20.16
ENERGY STAR® TM-21 Calculator
Note: Users should download a new copy of this calculator for each use, to ensure use of the most up-to-date version of the calculator. Users are encouraged to bookmark the hyperlink to this calculator. Project-specific copies complete with calculations may be saved on a local drive. This calculator is based on the Illuminating Engineering Society’s TM-21-11: Projecting Long Term Lumen Maintenance of LED Light Sources and Addendum A for TM-21-11: Projecting Long Term Lumen Maintenance of LED Packages. Calculator results have been reviewed by the U.S. National Institute of Standards and Technology (NIST). Calculations are locked; only data entry cells may be modified. Calculator inputs are entered on the second tab, with instructions. The calculator may be used with one, two or three case temperatures. Inputting values on the second tab generates a complete TM-21 report on the Report tab. For calculating data with different test period lengths, use data from the time period equal to the shortest time period for all temperatures. Questions may be directed to lighting@energystar.gov.

## TM-21 Inputs
TM-21 Inputs
LM-80 Test Inputs
| Instructions |  | Description of LED Light Source Tested (manufacturer, model, catalog number) |  | Test Data for 85⁰C Case Temperature |  | Test Data for 105⁰C Case Temperature |  | Tested Case Temperature 3
| Yellow fields are completed by the user. Fields not used should be left blank. Cyan fields are calculated based on user entries. First, enter a description of the LED light source tested. Then complete the fields labeled "LM-80 Testing Details". Test duration must be at least 6,000 hours. If only one case temperature data set is to be used (no interpolation), complete only "Tested case temperature 1". For only two case temperature data sets, complete 1 and 2. Next, further to the right, in the corresponding box(es) for each tested case temperature, enter the test data along with the time (in hours) at which each measurement was taken. Data entered must be normalized then averaged measured data (per TM-21 sections 5.2.1 and 5.2.2). If case temperatures have different test durations, enter data up to the lowest of the test durations for all of the case temperatures. Enter drive current, in-situ temperature data and the percentage of initial lumens to project to in the fields labeled "In-Situ Inputs". Results can be tailored to estimate lumen maintenance at a specific time by entering a value (t) in the yellow field. A complete TM-21 report will appear on the next tab labeled "Report". |  | Lumileds,LUXEON 5050 |  | Time (hours) | Lumen Maintenance (%) | Time (hours) | Lumen Maintenance (%) | Time (hours) | Lumen Maintenance (%)
[5 empty] | 0 | 100% | 0 | 100%
[5 empty] | 1000 | 100.1% | 1000 | 99.91%
[5 empty] | 2000 | 99.82% | 2000 | 99.6%
[5 empty] | 3000 | 99.63% | 3000 | 99.31%
[5 empty] | 4000 | 99.38% | 4000 | 99%
|  |  | LM-80 Testing Details |  | 5000 | 99.18% | 5000 | 98.72%
|  |  | Total number of units tested per case temperature: | 20 | 6000 | 98.9% | 6000 | 98.42%
|  |  | Number of failures: | 0 | 7000 | 98.67% | 7000 | 98.14%
|  |  | Number of units measured: | 20 | 8000 | 98.39% | 8000 | 97.82%
|  |  | Test duration (hours): | 12000 | 9000 | 98.11% | 9000 | 97.47%
|  |  | Tested drive current (mA): | 200 | 10000 | 97.8% | 10000 | 97.11%
|  |  | Tested case temperature 1 (Tc, ⁰C): | 85 | 11000 | 97.44% | 11000 | 96.75%
|  |  | Tested case temperature 2 (Tc, ⁰C): | 105 | 12000 | 97.05% | 12000 | 96.32%
Tested case temperature 3 (Tc, ⁰C):
In-Situ Inputs
|  |  | Drive current for each LED package/array/module (mA): | 193.9
|  |  | In-situ case temperature (Tc, ⁰C): | 57.5
|  |  | Percentage of initial lumens to project to (e.g. for L70, enter 70): | 70
Results
|  |  | Time (t) at which to estimate lumen maintenance (hours): | 50000
|  |  | Lumen maintenance at time (t) (%): | 86.23%
|  |  | Reported L70 (hours): | >72000

## Product Inputs
Calculations: | 2
Minimum Case Temperature (Ts,1) for Extrapolation (K): | 358.15
α1 | 3.134e-06 | Table 1: Report at each LM-80 Test Condition
B1 | 1.0085 | Case Temperature 1 |  | Case Temperature 2 |  | Case Temperature 3
Maximum Case Temperature (Ts,2) for Extrapolation (K): | N/A | Temperature (⁰C): | 85 | Temperature (⁰C): | 105 | Temperature (⁰C):
α2 | N/A | Temperature (⁰K): | 358.15 | Temperature (⁰K): | 378.15 | Temperature (⁰K):
B2 | N/A | α: | 3.134e-06 | α: | 3.5899e-06 | α:
Ea/kb |  | B: | 1.0085 | B: | 1.0063 | B:
|  | Calculated L70 (hrs): | 117000 | Calculated L70 (hrs): | 101000 | Calculated L70 (hrs):
kb (eV/K) | 8.6173e-05 | Reported L70 (hrs): | >72000 | Reported L70 (hrs): | >72000 | Reported L70 (hrs):
Ea (eV)
A
B0 | 1.0085 |  |  | Table 2: Report for Interpolation (based on in-situ temperature)
In Situ Case Temperature (Ts,i) (K): | 330.65
αi | 3.134e-06
Calculated L70 (hrs): | 117000
Reported L70 (hrs): | >72000

## TM-21 Projection
Number of Samples Tested: | 20 | Number of Samples Tested: | 20 | Number of Samples Tested: | 20 | Ts,1 (⁰C) | 85
Number of Failures: | 0 | Number of Failures: | 0 | Number of Failures: | 0 | Ts,1 (K) | 358.15
Number of Samples Measured: | 20 | Number of Samples Measured: | 20 | Number of Samples Measured: | 20 | α1 | 3.134e-06
DUT drive current used in the test (mA): | 200 | DUT drive current used in the test (mA): | 200 | DUT drive current used in the test (mA): | 200 | B1 | 1.0085
Test duration (hrs): | 12000 | Test duration (hrs): | 12000 | Test duration (hrs): |  | Ts,2 (⁰C)
Test duration used for projection (hr to hr): | 6000 | Test duration used for projection (hr to hr): | 6000 | Test duration used for projection (hr to hr): |  | Ts,2 (K) | N/A
Tested case temperature (⁰C): | 85 | Tested case temperature (⁰C): | 105 | Tested case temperature (⁰C): |  | α2 | N/A
α: | 3.134e-06 | α: | 3.5899e-06 | α: |  | B2 | N/A
B: | 1.0085 | B: | 1.0063 | B: |  | Ea/kb
Calculated L70 (hrs): | 117000 | Calculated L70 (hrs): | 101000 | Calculated L70 (hrs): |  | A
Reported L70 (hrs): | >72000 | Reported L70 (hrs): | >72000 | Reported L70 (hrs): |  | B0 | 1.0085
[6 empty] | Ts,i (⁰C) | 57.5
[6 empty] | Ts,i (K) | 330.65
[6 empty] | αi | 3.134e-06

## TM-21 Report
TM-21 Report
| Table 1: Report at each LM-80 Test Condition | [5 empty] | Table 2: Interpolation Report
| Description of LED Light Source Tested (manufacturer, model, catalog number) |  | Lumileds,LUXEON 5050 |  |  |  | (projection based on in-situ temperature entered)
[7 empty] | Ts,1 (⁰C) | 85
[7 empty] | Ts,1 (K) | 358.15
| Test Condition 1 - 85⁰C Case Temp |  | Test Condition 2 - 105⁰C Case Temp |  |  |  | α1 | 3.134e-06
| Sample size | 20 | Sample size | 20 | Sample size | - | B1 | 1.0085
| Number of failures | 0 | Number of failures | 0 | Number of failures | - | Ts,2 (⁰C) | -
| DUT drive current used in the test (mA) | 200 | DUT drive current used in the test (mA) | 200 | DUT drive current used in the test (mA) | - | Ts,2 (K) | -
| Test duration (hours) | 12000 | Test duration (hours) | 12000 | Test duration (hours) | - | α2 | -
| Test duration used for projection (hour to hour) | 6,000 - 12,000 | Test duration used for projection (hour to hour) | 6,000 - 12,000 | Test duration used for projection (hour to hour) | - | B2 | -
| Tested case temperature (⁰C) | 85 | Tested case temperature (⁰C) | 105 | Tested case temperature (⁰C) | - | Ea/kb | -
| α | 3.134e-06 | α | 3.5899e-06 | α | - | A | -
| B | 1.0085 | B | 1.0063 | B | - | B0 | 1.0085
| Reported L70(12k) (hours) | >72000 | Reported L70(12k) (hours) | >72000 | Reported L70(12k) (hours) | - | Ts,i (⁰C) | 57.5
[7 empty] | Ts,i (K) | 330.65
[7 empty] | αi | 3.134e-06
[7 empty] | Reported L70(12k) at 57.5⁰C (hours) | >72000
|  |  | Report Generated By: |  |  | Notes:
Company:
Date:

## Calculations - Case Temp 1 (hidden)
Test Data for 85⁰C Case Temperature
Interval Dif. | Interval | Time (hrs) = x | Average Normalized Lumen Maintenance = y | ln(y) | xy | x2 | xlny
- | -
-
|  | 6000 | 98.9% | -0.011061 | -66.3657 | 36000000 | -66.3657
| 1000 | 7000 | 98.67% | -0.013389 | -93.7247 | 49000000 | -93.7247
0 | 1000 | 8000 | 98.39% | -0.016231 | -129.8481 | 64000000 | -129.8481
0 | 1000 | 9000 | 98.11% | -0.019081 | -171.728 | 81000000 | -171.728
0 | 1000 | 10000 | 97.8% | -0.022246 | -222.4561 | 100000000 | -222.4561
0 | 1000 | 11000 | 97.44% | -0.025933 | -285.2672 | 121000000 | -285.2672
0 | 1000 | 12000 | 97.05% | -0.029944 | -359.3265 | 144000000 | -359.3265
PASS | Sums | 63000 | 686.4% | -0.13788 | -1328.7162 | 595000000 | -1328.7162
Results
|  | Slope: | -3.134e-06
|  | Intercept: | 0.008508
|  | α: | 3.134e-06
|  | B: | 1.0085
|  | Calculated L70 (hrs): | 117000
|  | Reported L70 (hrs): | >72000

## Calculations - Case Temp 2 (hidden)
Test Data for 105⁰C Case Temperature
Interval Dif. | Interval | Time (hrs) = x | Average Normalized Lumen Maintenance = y | ln(y) | xy | x2 | xlny
- | -
-
|  | 6000 | 98.42% | -0.015926 | -95.5569 | 36000000 | -95.5569
| 1000 | 7000 | 98.14% | -0.018775 | -131.4261 | 49000000 | -131.4261
0 | 1000 | 8000 | 97.82% | -0.022041 | -176.329 | 64000000 | -176.329
0 | 1000 | 9000 | 97.47% | -0.025626 | -230.6299 | 81000000 | -230.6299
0 | 1000 | 10000 | 97.11% | -0.029326 | -293.2583 | 100000000 | -293.2583
0 | 1000 | 11000 | 96.75% | -0.03304 | -363.4384 | 121000000 | -363.4384
0 | 1000 | 12000 | 96.32% | -0.037494 | -449.9305 | 144000000 | -449.9305
PASS | Sums | 63000 | 682% | -0.18223 | -1740.5691 | 595000000 | -1740.5691
Results
|  | Slope: | -3.5899e-06
|  | Intercept: | 0.0062769
|  | α: | 3.5899e-06
|  | B: | 1.0063
|  | Calculated L70 (hrs): | 101000
|  | Reported L70 (hrs): | >72000

## Calculations - Case Temp 3 (hidden)
Insert Case Temperature 3
Interval Dif. | Interval | Time (hrs) = x | Average Normalized Lumen Maintenance = y | ln(y) | xy | x2 | xlny
- | -
-
PASS | Sums | 0 | 0% | 0 | 0 | 0 | 0
Results
Slope:
Intercept:
α:
B:
Calculated L70 (hrs):
Reported L70 (hrs):